## Slide 1
Onsite Wastewater Treatment System Installation Challenges

## Slide 2: Indian Hills / Parmalee Gulch area
Notes: Indian Hills / Parmalee Gulch Area is not too far from where the conference is being held. It is an area that has experienced increasingly contaminated ground water over the last century. The properties in red is the prohibition area. These properties are subject to Jefferson County’s OWTS standards for Indian Hills & Parmalee Gulch area 2022

## Slide 3: Jefferson County OWTS Regs
Permitting
  OWTS Standards for Indian Hills & Parmalee Gulch Area
  Net Nitrogen Reduction must be achieved
  Repairs on < 2 acres requires TL3N
  Annual maintenance required
Notes: These standards are a subset of Jefferson County’s OWTS regulations. The intent of these standards is prohibit the discharge of additional nitrate from OWTS and decrease the discharge of nitrate.
The county’s research and modeling has found that people can produce 2.7 KgN (kilograms of nitrate)/ person / year
By upgrading an existing TL1 system to TL3N we can reduce the nitrogen loading by over 70%

## Slide 4: Indian Hills 23573 Moqui Road 2-bedroom residence OWTS Replacement
Challenges
  Clay (type 4 soil)
  0.44 acres
  Owners want to save trees in yard as much as possible
  Owners paying out of pocket
  Setbacks to wells
Notes: It is somewhat rare for this area to have a type 4 soil; however, this property had two 6-7 foot deep test pits that ribboned out to a type 4 clay.
Lot was very small. The area for the new STA was only 50 feet wide
Owners wanted to save trees if possible
Owners are paying out of pocket and prefer to keep capital costs low

## Slide 5: Single-family residence 300-GPD New System specs
  500-Gal poly tank for first compartment
  Norweco Singulair Green 960 with Hydro Kinetic Bio Film Reactor
  500-Gal poly discharge tank
  Geoflow headworks and 1,000 sq. ft. of Geoflow drip STA
Notes: We have had feedback from pumping companies that norweco tanks require pumping more often to keep up with the annual maintenance. We saw this as an opportunity to add a 500 gallon tank prior to the treatment unit and this could be compared over time to a similar system that does not have a 500 gallon tank prior
Norweco now provides a TL3N system that adds a Hydro Kinetic Bio Film Reactor to the system. The ongoing costs might be slightly higher than a recirculating media filter; such as the power consumption and the replacement aerators; however the upfront costs are somewhat lower.
500 gallon discharge tank. Colorado requires dosing with higher level treatment.
The area for the STA that we had to work with had some trees and was only 50 feet wide. We needed at least 1,000 sq ft so a bed type STA would have been around 28 – 30 feet long and 30 to 36 feet wide. With the slope of the property it would have required terracing out the backyard and wiping out most of the trees. And possibly some sand for leveling the chambers or sewer rock.
  This is why we decided to use drip dispersal.

## Slide 6: Existing and proposed system

## Slide 7: 23573 Moqui Road, Indian Hills view from the road
Notes: View of the trees that were saved. View is from the road looking south.

## Slide 8
Notes: Notice the drip tubing is only 10 to 12 inches deep and is capable of being routed around trees with minimal disturbance to the property.

## Slide 9
Notes: Existing septic tank was underneath an existing deck. The tank had to be abandoned, and the building sewer bypassed down to the new tanks.

## Slide 10
Notes: Geoflow headworks plumbing and final grade photos

## Slide 11: Indian Hills 5702 Santa Clara Road 2-bedroom residence Tank Replacement
Challenges
  Indian Hills Prohibition area
  Nowhere for an alternate STA that meets 200 foot well setback
  Very limited access
  0.233 acres
  Large deck in the way
  Any materials or equipment had to go down over a retaining wall
  Setbacks to house, property lines and existing STA
Notes: This site is also located in the Parmalee gulch prohibition area.
There is no where an alternate STA can be located that meets the 200 foot setback in the future. This means that Jefferson county will require HLT as part of the tank replacement.
All materials and equipment will have to work its way over an old tall retaining wall
Setbacks to house property lines and existing STA will come into play

## Slide 12: 5702 Santa Clara Road, Indian Hills 300 GPD Tank replacement specs
2 compartment Orenco Meander tank
  Concrete was not an option over the retaining wall.
  Meander tank is not as long as other tanks
  We were able to stack the AX20 pod on top of the tank.
Orenco’s AdvanTex AX20 pod for TL3N
  Not enough room to use an AXRT unit
24” diameter pump basin due to limited space
  Colorado requires dosing with HLT
Existing soil treatment area to remain in use.
Notes: We decided to use poly tank. Concrete tank would have required a crane.
The traditional 3 compartment septic tanks are around 13 feet long while the Meander tank if less than 9 feet in diameter.
A traditional 2 compartment tank and an AXRT unit would not fit.

## Slide 13
Notes: View of the retaining wall from up top.

## Slide 14
Notes: Design Site plan

## Slide 15
Notes: Profile and installation photo

## Slide 16
Notes: Installation Photos

## Slide 17
Questions?

## Slide 18
Thank You