## Slide 1
A PRACTICAL
GUIDE TO DRIP SYSTEMS

## Slide 2
WELCOME
Sean McGuigan
25+ years
Patented inventor
Technical Sales Manager
Septic licenses in three states
Specialties: designing, quoting, and training on treatment systems
Your presenter today is

## Slide 3
People
Oriented
Preserve
Sustain
One Place Solutions
Notes: Who we are:
Anua focuses holistically on People, Planet, and Solutions to ensure optimum outcomes.
We are People oriented. We listen and collaborate. We care about the planet. We preserve and sustain.
We offer solutions. Our One Place Solutions is simple and flexible.

## Slide 4
Notes: Anua offers a One Place solution to collect, treat, and disperse or reuse wastewater in a responsible and effective way.
We have manufacturing locations in Greensboro, NC since 1993 and in Boyne City, MI (Sim/Tech since 1998).
We have worldwide customers and distribution.

## Slide 5
TODAY’S GOALS
Drip System Basics
  Overview
  System Components & Functions
1.
Maintenance
Routine
  Inspection & Cleaning
2.
Essential
Design Basics
  Walkthrough
  Critical Parameters of Parts
  Design & Calculations
3.

## Slide 6
Drip System Basics
1.
Overview

## Slide 8
Drip System Basics
1.
System Components
& Functions

## Slide 9
Notes: Use adequate size, minimum isn’t the best. Flow EQ helps with size.
Access to the tank, risers to grade.
Access to the pump(s), unions near the lid.
Access to the floats, float trees with plenty of slack.
Access to secondary filters.

## Slide 10
Drip Pump Tank
  Use adequate size
  Access to:
    Tank
    Pumps
    Floats
    Secondary filters
1
Notes: Use adequate size, minimum isn’t the best. Flow EQ helps with size.
Access to the tank, risers to grade.
Access to the pump(s), unions near the lid.
Access to the floats, float trees with plenty of slack.
Access to secondary filters.

## Slide 11
Turbine Pumps
  Selection order:
  Must meet minimum system pressure
  Higher flow rate > 4 GPM is better
2
Notes: Turbine pumps are used for drip system instead of normal effluent pump.
Turbine pumps are sized to meet minimum pressure first then selected for GPM.
Pressure requirement of the system are first looked at and then the higher flow rate pump should be picked in that series.
Flows to a drip system should be at least greater than 4 GPM.

## Slide 12
Turbine Pumps
  Overcome system TDH to flush
  Sufficient GPM required
  After meeting TDH, higher flow rate preferred
  Velocity aids performance
2
Notes: Need to overcome system TDH to properly flush drip tubing.
Need to pump enough GPM to flush components.
Turbine pumps are designed for this type of flow, effluent pumps are not.
Rule of thumb, after TDH is satisfied, higher flow rate pump is preferred.
Velocity is your friend, but bigger isn’t always better.

## Slide 13
Sim/Tech
No-Vault Filters
  Turbine pumps have small intake area
  External filtration, 1/16” great add-on
  Not required
Notes: Turbine pumps have a small intake area
Great idea to add external filtration for the turbine pump; 1/16” is a nice size (add on, not requirement)

## Slide 14
Sim/Tech
Pressure Filters
  Secondary filter
  Installed between pump and headworks filter
    Add-on for coarser filtration
Notes: The secondary filter is placed after the pump but before the drip system's headworks filter.
If the water quality isn't as clean, this pressure filter serves as an add-on to provide additional coarse filtration.
It’s installed in-line between the pump and the headworks, ensuring that the water undergoes extra filtration before reaching the drip head.

## Slide 15
Sim/Tech Float Tree Kit
  Floats:
    ALWAYS on a separate float tree
    NEVER mounted on pump line
Notes: Floats should always be on a separate float tree
Should never be mounted on pump line (because pump vibrates)

## Slide 16
Control Panels
– Residential & Commercial
3
Notes: Needs to adequately perform the functions required.
Timing on/off, flushing functions, timing to zones if needed.

## Slide 17
DripFilterECO – Residential Headworks
Auto washdown and field flush
4
Notes: The more filter the better
ACCESS to components, ALWAYS
Auto washdown and auto field flush should be the MINIMUM, use best practice.

## Slide 18
DripFilterECO – Residential Headworks
More filter is better
Components: ALWAYS accessible
4
Notes: The more filter the better
ACCESS to components, ALWAYS
Auto washdown and auto field flush should be the MINIMUM, use best practice.

## Slide 19
Screen Filters
vs. Disc Filters
  130 microns
Notes: This is a choice to use screen or disk filter. The disk filter is 3D. The more filter area is better

## Slide 20
Solenoid Valves (External)
  Better zone management
  Air release valves may be needed
    Design dependent
    Less maintenance
Notes: Internal solenoid valves NOT preferred
Prefer External solenoid valves. Better zone management, different timer settings possible.
May need air release valves, design dependent.

## Slide 21
DripFilterECO
– Commercial
Headworks
Filter headworks are scalable
Notes: Filter headworks are scalable. Multiple configurations available.
Options include filters only, zone valves only, or filters/zone valves combo.
Can be plumbed together like "train cars" based on the number of filters and zones required.
Jumbo headworks is 4.5’x7’, the size of a piece of plywood.

## Slide 22
Flowmeters
  Use for system monitoring

## Slide 23
Pressure Regulators
  Accessible for maintenance
  Drip tubing < 50 PSI
  Use for each zone
5
Notes: Drip tubing shouldn’t run over 50 PSI
Should be placed just before inlet manifold before each zone
If more than one zone is designed, Pressure Regulators are used at each zone
They have ratings on them for GPM and PSI

## Slide 24
Notes: Use adequate size, minimum isn’t the best. Flow EQ helps with size.
Access to the tank, risers to grade.
Access to the pump(s), unions near the lid.
Access to the floats, float trees with plenty of slack.
Access to secondary filters.

## Slide 25
Diverter Valves
  Need proper positioning
  Need air release valves
  Widely used
Notes: Need to be positioned correctly on the landscape.
Should have air release valves.
Are widely used

## Slide 26
Check Valves
More than one zone
  Use to isolate individual zones
Must be accessible for maintenance
Notes: If more than one zone is designed, Check Valves are used to isolate individual zones.
All of these must be accessible for maintenance. (Basins or Boxes)
They will leak someday

## Slide 27
Lockslip Fittings
Slip style headers most common
Couplings
  Joining a loop
  Splicing tubing
L’s
  For loops
  Go around things
6
Notes: The most common are the Slip style for the headers
The couplings are next and used for joining a loop or splicing tubing
L’s are for loops and to go around things
The brown locksilp is for 17mm tubing and black is for 16mm.

## Slide 28
Manifold Connection
6
Notes: This is a 1” x ¾” T and the slip fitting inserts and glues in.
The picture shown is a ½” socket x ¾” spigot is most popular

## Slide 29
Manifold Connection
6

## Slide 30
Lockslip Loops & Risers
7

## Slide 31
Kinetic Air Release Vacuum Breakers
Drip tubing should NEVER be under negative pressure
Need 2 per zone:
  High point of pressure side
  Return side of manifold
Only points to accurately check system pressures
8
Notes: Break vacuum and release some air.
Kinetic means motion, once closed no more air is released.
Most importantly, vacuum breaking, drip tubing should NEVER be under negative pressure.
Need at least one of these at the high point of the pressure side manifold and the return side manifold (one at each side) for each zone.
These are the only points that accurately check the pressure in the system.

## Slide 32
Continuous Air Release
Vacuum Breaker Valve
CONTINUOUSLY releases air and breaks vacuum
Used for systems with:
  Long runs
  Dips
  Valleys
8
Notes: Break vacuum and release air CONTINUOUSLY
Systems that have long runs, dips and valleys should use Continuous Air Release Valves
May be needed in multiple locations.

## Slide 33
Air Release/Vacuum Breakers
Must be accessible
CORRECT place to check system pressure
8
Notes: Air release vacuum breaker must be accessible
The CORRECT place to check the system pressure

## Slide 34
Valve Boxes
Notes: All parts need to be accessible for maintenance
Check valve PMRs
Air Vac releases etc.

## Slide 36
WaterflowPRO Drip Tubing
  PC
  0.6 or 0.9 GPH
  Optimal PSI 20-50
  12” or 24” emitter spacing
9
Notes: Different Diameters, 16mm & 17mm others can be made.
Different nominal flow rates from Emitters
Flow rates on PC PRO Tubing are .6 gph or .9 gph with optimal PSI range 20-50, but over 60 PSI fitting malfunctioning may occur.

## Slide 37
WaterflowPRO Drip Tubing
9
Notes: Once pressure releases water oozes out of the tube.
Compensating Chamber operates under pressure.

## Slide 38
Geoshield®
  Antimicrobial lining
  Prevents biofilm build-up inside
  Flushing works better even at lower velocity
Geoshield® lining
9
Notes: Geoshield® antimicrobial lining prevents biofilm build-up inside tubing.
Allows flushing to work better, also at lower velocity.

## Slide 39
Rootguard®
  Patented nano-Rootguard® band prevents root intrusion
9
Notes: Patented nano-Rootguard® band Protects against root intrusion
Pre-emergent and does not leach out

## Slide 40
9
Notes: Three styles of connections used.

## Slide 41
Maintenance Routine
2.
Inspection & Cleaning

## Slide 42
Maintenance Routine
  Pump
  Auxiliary Filters
  Headwork Filters
  Flushing
  Vacuum Breakers
  Inspection
  Valves

## Slide 43
Pump
  Follow pump and treatment manufacturer maintenance guidelines
  Monitor and remove solids from pump and treatment units as needed
SimTech Tru Core Sludge Sampler
Notes: Check with pump and treatment plant manufacturer for maintenance recommendations.
Check for solids build-up in pump chamber and treatment unit/septic tanks. Pump out when needed.

## Slide 44
Auxiliary Filters
  Clean auxiliary filters
    Septic tank
    No-Vault
Pleated Gravity Filters
Notes: Maintain and clean auxiliary filters – septic tank filter, no-vault filter

## Slide 45
Headwork
Filters
  Clean/replace headwork filters
Notes: Clean and/or replace headwork filters

## Slide 46
Flushing
  Flushing:
    Activate pump
    Open return line valve
    Flush each zone same duration as dose
  Reset return line valve
  Check field pressure and flow rate
PRESSURE
OPEN RETURN
FLOW
PUMP
RESET
FLUSH
Notes: Activate pump and open return line valve. Flush each zone for same time as dose.
Reset return line valve to original setting and check field pressure. (Check flow rate if system includes flow meter).

## Slide 47
Vacuum Breakers
  Check for proper operation
  Clean
Notes: Check vacuum breakers for proper operation. Clean them.

## Slide 48
Inspection
  Fields
    Pooling of water
    Dry and wet areas
  Record in log
    Date
    Counters
    ETM
    Field pressures, etc.
Notes: Check field for any signs of distribution issues – pooling of water, dry area in some and wet in other.
Record date, counters, ETM, field pressure(s), etc. in log.

## Slide 49
Solenoid Valves
  Remove, disassemble and clean
    Every 2 – 3 years
  Reset control system for auto operation
Notes: If Pressure Reducers (PMR) check valves or electric solenoid valves are used:
remove, disassemble and clean every two to three years to insure long life and continued operation.
Reset control system for auto operation.

## Slide 50
Essential Design Basics
3.
Walkthrough

## Slide 51
Design Walkthrough
  For designs < 2,000sq.ft
  Critical parameters of parts
  Design Basics
  Calculations simplified
Notes: Starting a design 1,000 sqft and smaller.
Critical parameters of parts, design basics, design calculations simplified.
Florida rules need to be followed.

## Slide 52
Worksheet
Notes: Starting a design 1,000 sqft and smaller.
Critical parameters of parts, design basics, design calculations simplified.
Florida rules need to be followed.

## Slide 54
Essential Design Basics
3.
Critical Parameters of Parts

## Slide 55
Design Parts
  Turbine pump
  PVC plumbing
  Automatic headworks
  Panel
  Drip tube
  Air vacuum release
  PMR valve

## Slide 56
Turbine
Pump
  20 GPM is BEST

## Slide 57
PVC Plumbing
  Out: 1.25" BEST
  Flush return: ≤ 1" OK
  Distance:
    100' out
    100' back
  Pump to riser: 1.25"
  Elevation up to 20ft
Notes: 1" is better for out, can use smaller for flush return
Distance less than 100' out and 100' back
Use 1.25" on pump to riser outlet
Elevation up to 20 ft

## Slide 58
Automatic Headworks
  Automatic = controlled (Solenoids)
  Some manufacturers use switching flushing filters AND solenoids for field
Notes: Florida rules: "All systems shall incorporate an automatic mechanism for backwashing or flushing the drip lines and filters"
To be automatic it must be controlled, that means Solenoids
Some manufactures use switching flushing filters AND solenoids for field

## Slide 59
Panel
  Specifications
    3 floats MINIMUM
    Time-dosed over 24hr
24 HR
3 FLOATS
Alarm
EXCESS
Notes: Specifications
3 floats minimum
Rule: "Drip irrigation systems shall be time-dosed over the 24-hour period. Demand control dosing shall override timed-dosing in periods of flow where timed dosing cannot accommodate the excessive flow."

## Slide 60
Drip Tube
  Spacing between runs:
    MAX 24"
    MIN 6“ or less
  BEST for small systems
Notes: WFPC-16-4-12
Max spacing 24” between Runs, Min Spacing 6” Between Runs
Best tube for small systems
Pump needs GPM above 4.5 GPM for 300’ of Drip Tube

## Slide 61
Air Vacuum Release, PMR Valve
  MINIMUM 2 Air Vacs
    High point of pressure
    Return lines
  PMR after filter
Notes: Minimum Two Air Vacs
– Air vacs go on the high point of the pressure and the return lines
PMR after filter, 40 PSI is a good choice.

## Slide 65
THANK YOU
FOR YOUR ATTENTION

## Slide 66
Contact Me For Anything Septic
e sean.mcguigan@anua-us.com
t 603.348.7579
w geoflow.com
simtechfilter.com
anuainternational.com