## Slide 1: Troubleshooting and Repairing Onsite & Decentralized Systems
Ben Kele, Tim Woods, & Andrew Kele

## Slide 2: Climate Map of Australia

## Slide 3: Summer In Australia

## Slide 4: Australian On-Site & Decentralized Sites

## Slide 5: How is Failure Defined?
On-site and Decentralized systems fail (frequently)
Different stakeholders may have varying definitions of failure (in regards to importance to them)
  Owners
    Odor, noise, cost of operation, surface pooling, etc
  Regulators
    Water Quality, environmental impact, etc
  Manufacturers and Installers
    Frequency of call-outs, false alarms, etc
Failure can be caused by many factors

## Slide 6: How do you Define Failure?

## Slide 7: People…

## Slide 8: What Causes Failure
Original design
  Site inspection
  Information from the client
  System selection
    Fit-for-purpose
Lack of ongoing maintenance
  Institutional knowledge disappears…
System has reached the end of its working life
Changes in the site over time

## Slide 9: Failure Can be Slow

## Slide 10: Failure Can Be Putting Up With OK Performance

## Slide 11: Common Design Failures
Design
  Wastewater volume
  Inflow wastewater quality
  Inflow wastewater generation patterns
  Soil at site
Domestic/Commercial/Industrial
  NSF testing process
  Treatment system selection

## Slide 12
Ben’s Child Care Centre
Kids Not Picked Up on Time will be Taught to Swear

## Slide 13
Ben’s Tavern
You Can’t Drink All Day if You Don’t Start in the Morning

## Slide 15
Ben’s Gym
No, You Don’t Look Good in Lycra

## Slide 16
Ben’s Kebab Shop
Why Have Ab’s When You Can Have Kebabs

## Slide 17: Varying Inflow Water Quality
Child Care Centres
  Nappies, wet wipes, higher proportions of urine, typically not open at night
Tavern’s
  Higher proportions of urine, disinfectants, maybe a commercial kitchen (oil & grease), increased phosphorus concentration (spirits), open from late morning to late at night
Gyms
  Dilute wastewater from showers and often open 24 hours
Kebab Shop (fast food)
  Takeaway different wastewater from dine-in
  Oils & grease much higher; even with good quality greasetrap

## Slide 18: Unusual Water Quality Issues

## Slide 19: Installation issues
Site investigations
  Soil tests
  Set back distances
Training on installation crews
  Skills shortages
  Weather during installation
  Coordination of trades plumbers & electricians
Changes made by the client during the project delivery
Real Estate agents…

## Slide 20: Infiltration Issues

## Slide 21: Soil Testing
Foundation/Structural soil tests are not suitable for on-site wastewater analysis
Needs a sodicity analysis
  Exchangeable % of sodium (ESP)
  Cation exchange capacity (CEC)
  Organic carbon is also useful
For nutrient leaching
  Phosphorus absorption
    % clay
  Soil texture (sand)
    Risk of nitrogen movement
An understanding of salinity and the sodicity of the water being applied
Distribution of the treated water needs to be even

## Slide 22: Distribution Issues

## Slide 23: Operation and Maintenance
Lack of maintenance
  Major competitor is people doing nothing
  No such thing as maintenance free
Education of stakeholders
  Many people don’t understand that maintenance is required
Training staff
  Skill shortages
  USA doing much better than Australia in this area
Establishing a common-sense budget for ongoing maintenance

## Slide 24: Operation and Maintenance

## Slide 25: Trouble-Shooting a Failure
Some failures are more easy to work out than others
  Pump failures
  Pipe ruptures (above ground or in tank)
  Electrical faults (breakers, etc)
  Broken aerators
Some are harder to track down
  Clogged or always open non-return/check valves
  Splits in air lines under the water
  Buried pipe rupture/s
  Intermittent faults
  Alarm failures
  Issues with floats/level sensors
Some are very difficult
  Treated water quality
  Dispersal field failures

## Slide 26: Water Quality Issues
These can be hard to trouble shoot
We don’t often test for the things that can cause issues with water quality
  For example a high BOD5 or nitrogen result requires additional testing to diagnose the problem
  Total organic carbon test is often required
  Dissolved oxygen
  Sometimes a sulphur test
  Beneficial microorganism count can be helpful
    Non-fastidious heterotrophic bacteria
Water quality issues can be caused by strange things; such as 2-in-1 shampoo and conditioner

## Slide 27: Water Quality Issues
Standard tests
  pH, salinity (EC or TDS), BOD5, nitrogen, phosphorus, total suspended solids, fecal coliforms, etc are useful but quite often miss what is causing a treatment problem in a on-site or decentralized system
Diagnostic tests may include
  The different types of nitrogen (ammonia, nitrite, nitrate, etc)
  Chemical oxygen demand and total organic carbon
  Sulphur (essential nutrient for many beneficial microbes)
  Heavy metals
  Comparison of the different salts; sodium, potassium, calcium & magneisum
  A wider microorganisms analysis
Water quality problems can occur because something is in too low a concentration or too high a concentration
  Outside the typical range
  Total organic carbon is an example

## Slide 28: Water Quality Issues
Hydraulic retention time
  Short circuits are a frequent cause of failure
  Just because a tank has a certain volume doesn’t mean that the water will be in that space for a specific length of time
  Dye tests can be very useful
    Determine the actual residence time
  Peak flows are easy to underestimate
  Installing a larger tank right from the start can prevent problems from occurring later

## Slide 29: Repairs
A lot of people just suggest replacement rather than repairing or adjusting an existing system
  Sometimes replacement is the right answer
You can learn a great deal by troubleshooting and repairing systems
  This can improve your designs
  You can also get very frustrated…
Understanding what has gone wrong and why is key to fixing the problem
Many of my trouble-shooting projects have started by fixing ‘dodgy’ repairs that misdiagnosed the original problem

## Slide 30: Repairs: Aeration
Volume of air
Surface area of air
Temperature of air
Oxygen transfer rate
Closely tied to the health of beneficial microorganisms
Can be too much in case of nitrogen transformation
Reducing air volume for energy efficiency can be a false saving

## Slide 31: Beneficial Bacteria
Beneficial bacteria
  Growth media
  Retention time
  Different oxygen conditions
  Harmful chemicals
  Environmental conditions
  Temperature
Naturally present
  Can be purchased as an additive
Plenty of chemicals can impede their performance and impact on water quality
Don’t like intermittent flows

## Slide 32: Hydraulic Retention Time
An undersized system is always undersized
But some systems can be too big as well
  Not enough food for the system to work as designed
Biological systems typically need the longer periods of time
Some tanks can have baffles retro-fitted
Changes in pipework can also help with retention time

## Slide 33: Hydraulic Retention Time

## Slide 34: Soil Repair
Dispersal area or part of the treatment system?
  Such as irrigation versus mounds
Application rate
  Even distribution
  Intermittent dosing (sequencing valve)
  Pump controller with small doses; rather than floats which send a relatively large volume of the tank
Basic good gardening advice
  Gypsum and organic carbon (compost)
  This can be counter-intuitive, as compost has a high BOD5/COD
  Difference between applying to soil and disposing to water
  Gypsum repairs soil from the adverse impacts of sodicity

## Slide 35: Soil Repair

## Slide 36: Case Study

## Slide 37: Case Study

## Slide 38: Case Study

## Slide 39: Case Study

## Slide 40: Case Study

## Slide 41: Case Study

## Slide 42: Case Study

## Slide 43: What Can Be Achieved?

## Slide 44: Conclusion
You can learn a great deal about how wastewater treatment systems operate by trouble-shooting and repairing existing installations
You may need a different set of diagnostic tests to work out what is going wrong, than your standard water quality tests
You need to look back to how the system was originally designed, how it was installed, and how it is has been operated and maintained, to fully understand which is going on at the site.
People have different definitions of failure
Not everything can be repaired; sometimes starting again is the right answer
Learning from other peoples mistakes can be less stressful than learning from your own…